Models:	  AZON-I-E   Electric duct heaters with factory installed discharge thermostats

AZON-II-E   Electric duct heaters with field installed discharge thermostats

GUIDE SPECIFICATION

(Suitable for the CSI Master Format)

Electric Duct Heaters

- Electric duct heaters shall be Acu-Zone™ model AZON-I-E or AZON-II-E manufactured by Acutherm, Hayward, CA.

- Each unit shall be a complete open coil duct heater with modulating SCR proportional controller, airflow sensor, discharge air sensor and room thermostat to provide a constant supply air temperature at both design and very low airflows.  Units that do not provide a constant supply air temperature shall not be allowed.

- The discharge thermostat shall be field adjustable. It shall be factory set for a constant supply temperature of approximately 90˚F/32˚C to minimize room air stratification. The discharge air temperature thermostat shall be factory installed in the AZON-I-E models and shall be field installed by others for AZON-II-E models. An electronic mode control room thermostat shall be supplied for field installation by others.

- The unit shall be packaged in a heavy duty galvanized steel box complete with electric heating elements, controls and safety devices for over temperature control. The controls enclosure shall be NEMA 1 and a cover shall be easily removable for access to a single point electric supply connection and a room thermostat connection. AZON-II-E models also have a discharge air thermostat connection. The unit shall be CSA (C & US) labeled for safety and reliability.

- Electric heating elements shall be open coil type constructed from the highest-grade nickel-chrome resistance wire ensuring that the wires will not age or oxidize to provide longer life. Each unit shall have an automatic reset thermal cutout, a safety feature to prevent overheating, that will reset after cooling down. Each unit shall also incorporate a manual reset thermal cutout for redundancy and to prevent the heater frame from overheating.
Model AZON-I-E shall have a round inlet and outlet as scheduled.  Inlet and outlet for model AZONE-II-E shall be either round, square or rectangular as scheduled.

- The manufacturer shall warrant that all Acu-Zone electric heaters shall be free from defects in materials and workmanship for a period of two years from date of shipment.

.